## SEPT. 09-04-2023
TEMPERATURE RISE CATEGORY CLASSIFICATION / RECOMMENDED ACTION
( Temperature Difference Between Equipment and Ambient Temperature )
| 1°C - 10°C | 1st Stage | ADVISORY | Possible deficiency or Overheating; Warrant an Investigation
| 11°C - 20°C | 2nd Stage | INTERMEDIATE | Indicates probable Deficiency or Overheating; Repair as time permits
| 21°C - 40°C | Serious | SERIOUS | Developed Overheating; Monitor until corrective action is Accomplished as soon as possible
| 41°C | Critical | IMMEDIATE | Major Dicrepancy or Overheating; Repair Immediately
List of Equipments with Anomaly
Report No. | Location | Equipment ID | Component | Category of Anomaly | Evaluation | Recommendation | Corrective Action Taken | Date | Done by
1 | Plant 1, Ground Floor, Electrical Room | MSB-3 | 300AT, 3P, CB.no.5 | 2nd STAGE INTERMEDIATE | Elevated temperature was detected and the problem persists. Though, the situatuon is still manageable and allowable. | 1. For close monitoring. | 1. Check/clean terminals & Retighten all bolted connections. | 2023-12-28 | SMART-TECH
2
3
4
5
List of Equipments with Normal Thermal Signature
Report No. | Location | Equipment ID | Component | Category of Anomaly | Evaluation | Recommendation | Corrective Action Taken | Date | Done by
1 | Perimeter | FIRST PRIVATE POLE |  |  | No Thermal Anomalies Detected.
2
3
4
5
***** Nothing Follows *****
Inspected/Evaluated by: |  |  |  | Reviewed by: |  | Approved by: | Customer Representative:
Karl Jason V. Nullas ▼ |  |  |  | Nash Nichol A. Collao ▼ |  | Stephen F. Collao P.E.E. ▼ | Engr. Jovin P. Dumilig
Asst. Thermographer |  |  |  | Asst. Technical Staff |  | Certified Thermographer-I | Facilities Manager